SCOPE OF WORK

Commercial Office Fitout

| Project: | 5,000 SF Office Fitout — Midtown Manhattan |
| --- | --- |
| Location: | 25th Street Corridor, New York, NY 10001 |
| Space: | 50’-0" x 100’-0" — 10’-0" Ceiling Height |
| Budget: | $1,500,000 (All-In including FF&E) |
| Date: | March 28, 2026 |
| Prepared By: | [General Contractor Name] |
| Prepared For: | [Tenant / Client Name] |

TABLE OF CONTENTS

1. General Conditions & Project Management

2. Demolition & Abatement

3. Framing & Drywall

4. Doors, Frames & Hardware

5. Flooring

6. Painting

7. Ceiling

8. Millwork & Casework

9. HVAC / Mechanical

10. Plumbing

11. Fire Protection

12. Electrical

13. Fire Alarm

14. Low Voltage / Data / AV / Security

15. Architectural Glass & Specialties

16. Furniture, Fixtures & Equipment (FF&E)

17. Exclusions

18. Assumptions & Clarifications

1. GENERAL CONDITIONS & PROJECT MANAGEMENT

- Full-time on-site superintendent for duration of project (approx. 16-20 weeks)

- Project Manager assigned from preconstruction through closeout

- Weekly OAC meetings with documented minutes and action items

- Maintain updated CPM schedule with 2-week lookaheads

- DOB permits: Alt-2 work permit, plumbing, sprinkler, electrical permits

- Licensed expediter for all DOB filings and sign-offs

- Builder's Risk and General Liability insurance per lease requirements

- OCIP/CCIP enrollment if required by landlord

- Temporary protection of elevators, lobbies, and common areas per building rules

- Dumpster and hoist coordination with building management

- Daily cleanup and OSHA-compliant site safety program

- Material deliveries coordinated with building freight elevator schedule

- Final cleaning including windows, floors, and all surfaces

2. DEMOLITION & ABATEMENT

- Complete selective demolition of existing partitions, ceiling grid, and MEP as required

- Removal of existing flooring down to structural slab

- ACM survey (Type 3) by licensed environmental consultant prior to demo

- Lead paint testing on all painted surfaces

- Asbestos abatement of identified ACM materials by licensed abatement contractor with air monitoring

- NYC DEP ACP-5/ACP-7 filings for any abatement work

- Disconnect and cap all existing MEP services at points of origin

- Protect existing base building systems (risers, shafts, fire alarm loops)

- Debris removal via building-approved hauling contractor

- Slab patching and leveling after demo as required for new finishes

3. FRAMING & DRYWALL

- Metal stud framing per architectural drawings (3-5/8" and 2-1/2" steel studs at 16" o.c.)

- Full-height partitions from slab to deck where indicated for sound and fire rating

- 5/8" Type X gypsum board both sides on rated partitions (1-hour rating where required)

- Double-layer drywall at conference rooms for enhanced STC rating

- Shaft wall assemblies at mechanical/electrical rooms per code

- Fiberglass batt insulation (R-13 min.) in all rated and acoustic partitions

- Finishing to Level 4 on all exposed surfaces, Level 5 where specified

- Furring and blocking for millwork, TV mounts, grab bars, and heavy accessories

- Corner bead, control joints, and fire caulking at all penetrations

- Coordination with MEP trades for all in-wall rough-ins prior to close-up

4. DOORS, FRAMES & HARDWARE

- Hollow metal frames at rated locations, wood frames at standard locations

- Solid core wood doors (stain or paint grade per finish schedule)

- Frameless glass doors at conference rooms where indicated

- Commercial-grade lever hardware (Schlage or equal) with ADA-compliant handles

- Door closers on all corridor and rated doors per code

- Keying: master key system coordinated with building management

- Automatic door openers at main entry and ADA-accessible restrooms

- Kick plates, silencers, and thresholds as required

- Fire-rated door assemblies with labels and required UL hardware at all rated openings

5. FLOORING

- Moisture testing of concrete slab per ASTM F2170 (RH probe method)

- Self-leveling underlayment as required for flatness tolerance (1/8" in 10 ft)

- Luxury Vinyl Tile (LVT) in open office and circulation areas

- Carpet tile (Shaw, Interface, or equal) in private offices and conference rooms

- Porcelain tile in pantry/kitchen and restroom areas with waterproof membrane

- Transition strips at all material changes

- Base: 4" rubber or wood base throughout per finish schedule

- Walk-off mat/carpet at main entry

- Floor preparation including grinding, patching, and priming

6. PAINTING

- Prime and paint all new drywall surfaces (2 coats finish minimum)

- Accent walls per design intent with specified colors

- Touch-up paint on all existing surfaces to remain

- Paint all exposed mechanical/electrical rooms

- Paint all door frames (unless prefinished)

- Low-VOC paints (Benjamin Moore Aura or equal) throughout for LEED/WELL compliance

- Ceiling paint at exposed deck areas (if applicable) including structure, ductwork, and piping

7. CEILING

- 2x2 Acoustical Ceiling Tile (ACT) in open office areas (Armstrong or USG, NRC 0.70 min.)

- Suspended drywall ceiling in reception, conference rooms, and executive offices

- Exposed/painted deck with acoustic cloud panels in collaborative/lounge areas

- Access panels at all concealed valves, dampers, and equipment requiring service

- Ceiling grid and tile coordination with all MEP trades for diffuser, light, and sprinkler head locations

- Perimeter ceiling trim and reveals per architectural details

- 10'-0" ceiling height maintained throughout (coordinate all MEP routing above ceiling)

8. MILLWORK & CASEWORK

- Custom reception desk with stone or solid surface countertop

- Pantry/kitchen cabinetry: upper and lower cabinets with quartz countertops

- Pantry backsplash tile installation

- Built-in credenzas in executive offices

- Storage/coat closet built-ins with shelving and rods

- Mail/copy room millwork with sorting cubbies and countertop

- All millwork shop drawings submitted for approval prior to fabrication

- Wood veneer or laminate finish per design selections

9. HVAC / MECHANICAL

- Tap into base building chilled water / hot water risers (coordinate with building engineer)

- Fan coil units (horizontal concealed) serving perimeter zones

- Supplemental cooling: dedicated split system or VRF cassettes for server/IDF room

- Supply and return ductwork distribution (galvanized sheet metal) for 5,000 SF

- Linear slot diffusers in open areas, square diffusers in ACT ceiling areas

- Exhaust ductwork for pantry and restrooms per code (IMC requirements)

- DDC/BMS controls: new zone controllers tied to base building BMS (BACnet/IP)

- Programmable thermostats in all zones

- Kitchen hood exhaust (Type 1 or Type 2 per use) if full kitchen

- Refrigerant piping, insulation, condensate piping, and drain connections

- Test and Balance (TAB) by AABC/NEBB certified contractor

- Commissioning of all mechanical systems per spec

- NYC Mechanical Code compliance and DOB sign-offs

- Furnish O&M manuals, as-built drawings, and warranty documentation

10. PLUMBING

- Pantry/kitchen sink with hot and cold water connections

- Under-counter point-of-use water heater

- Dishwasher connection (supply, drain, electric)

- Instant hot water dispenser at pantry if specified

- Restroom fixtures: water closets, urinals, lavatories per code count

- ADA-compliant fixtures and accessories in all restrooms

- Floor drains in restrooms and pantry with trap primers

- Domestic water distribution (copper or PEX per code)

- Sanitary waste and vent piping

- Water meter and backflow preventer installation if required by building

- Gas piping for kitchen equipment if applicable

- DOB plumbing permit and sign-off

11. FIRE PROTECTION

- Relocate and add sprinkler heads to match new reflected ceiling plan

- Upright, pendant, and concealed heads per ceiling type and finish

- Hydraulic calculations by PE and submission to DOB

- Sprinkler drain-down coordination with building riser

- Fire caulking at all penetrations through rated assemblies

- DOB sprinkler permit and sign-off

- Furnish as-built sprinkler drawings

12. ELECTRICAL

- New electrical panel(s) fed from building switchgear (200A typical for 5,000 SF office)

- Branch circuit wiring for all outlets, lighting, and mechanical equipment

- Duplex receptacles at workstations (1 per 50 SF min. per code, additional per furniture plan)

- Dedicated 20A circuits for pantry appliances (microwave, dishwasher, refrigerator)

- Dedicated circuit for server/IDF room with isolated ground

- LED recessed downlights in open office (2x2 or 2x4 troffers, or linear)

- Pendant or decorative fixtures in reception, lounge, and conference rooms

- Under-cabinet task lighting in pantry

- Dimming controls (Lutron or equal) in conference rooms and executive offices

- Occupancy/vacancy sensors per NYC Energy Code

- Emergency and exit lighting per code

- Electrical metering (sub-meter if required by lease)

- DOB electrical permit and sign-off

- As-built electrical drawings and panel schedules

13. FIRE ALARM

- New smoke detectors and heat detectors per NFPA 72 and new layout

- Horn/strobe devices in all occupiable spaces per ADA spacing requirements

- Manual pull stations at exits

- Duct smoke detectors on AHUs/fan coils serving over 2,000 CFM

- Tie into base building fire alarm panel (coordinate with building FA vendor)

- Fire alarm riser diagram and shop drawings

- FDNY acceptance testing and Certificate of Approval

- DOB fire alarm permit and sign-off

14. LOW VOLTAGE / DATA / AV / SECURITY

- Cat6A structured cabling: 2 drops per workstation, additional at conference and huddle rooms

- Fiber optic demarc from building telco room to tenant IDF

- IDF/server room buildout: ladder rack, cable management, grounding, UPS connection

- Wireless Access Points (WAPs): ceiling-mounted, locations per RF survey

- Conference room AV: 75" display, soundbar, camera, wireless presentation system

- Huddle room AV: 55" display with wireless dongle

- Access control: card readers at main entry and server room (integrate with building system)

- CCTV: IP cameras at entry points and reception

- Audio/visual rough-in and final connections per AV consultant drawings

15. ARCHITECTURAL GLASS & SPECIALTIES

- Full-height glass partitions at conference rooms (1/2" tempered clear glass)

- Glass entry doors with patch fittings or pivot hardware

- Film or frosting bands on glass per design (privacy at 42" AFF)

- Interior signage: suite entry, room IDs, ADA-compliant restroom signs

- Toilet partitions and accessories (stainless steel or solid phenolic)

- Mirrors, soap dispensers, paper towel dispensers in restrooms

- Window treatments: motorized roller shades at exterior windows

16. FURNITURE, FIXTURES & EQUIPMENT (FF&E)

- Open office workstations (benching system, Steelcase or Herman Miller) with monitor arms and task lighting

- Ergonomic task chairs at all workstations

- Private office desks, credenzas, and guest chairs

- Conference table (seats 12-14) with integrated power/data, plus chairs

- Huddle room tables (seats 4-6) with power, plus chairs

- Reception desk chair and guest seating (sofa + lounge chairs)

- Pantry/break room: dining table, chairs, refrigerator, microwave, coffee machine, dishwasher

- Lounge/collaboration area: soft seating, coffee tables, high-top tables with stools

- Storage: personal lockers, lateral file cabinets, bookcases

- Delivery, assembly, and installation of all furniture

- Furniture warranty documentation

17. EXCLUSIONS

The following items are specifically excluded from this scope of work:

- Base building HVAC system upgrades or modifications beyond tenant riser taps

- Structural modifications (new openings, reinforcements, slab penetrations requiring SE)

- Exterior facade work, window replacement, or roof work

- Generator or UPS equipment (beyond receptacle provisions)

- Kitchen equipment beyond standard pantry appliances

- Specialized acoustic treatments (sound masking, recording studio-grade isolation)

- After-hours HVAC charges by building during construction

- Building management fees or landlord review fees

- Tenant's personal property, artwork, or decorative accessories

- IT equipment (servers, switches, routers, computers, phones)

- Moving and relocation services

18. ASSUMPTIONS & CLARIFICATIONS

- Space is delivered in as-is condition; existing conditions survey to be completed during preconstruction

- Building provides adequate electrical capacity (200A min.) and HVAC riser capacity for tenant load

- Work hours per building rules (typically 8AM-5PM M-F; overtime/weekend work at additional cost)

- All work performed under prevailing wage / union labor as required by building

- Landlord approval of plans required prior to permit filing

- Design team (architect and MEP engineer) engaged separately by tenant

- Hazardous materials abatement scope is estimated; final scope subject to survey results

- Building freight elevator available for material deliveries during designated hours

- No unforeseen conditions behind existing walls, above ceilings, or below slab

- All submittals reviewed and approved within 5 business days of submission

ACKNOWLEDGMENT & ACCEPTANCE

This Scope of Work is acknowledged and accepted by the undersigned parties:

General Contractor:	Tenant / Client:

_______________________________	_______________________________

Name:	Name:

Title:	Title:

Date:	Date: